## Worksheet 1
| Weekly or fortnightly (or after heavy rainfall events) | Intermediate | Annual
Pump | Strainer cleaning |  | Replacement or cleaning(prevention of clogging)
Small tubing/filtered water circulation | Verification/cleaning |  | Changes twice a year
Pipes | Verification/cleaning | Cleaning of removable segments | Replacement or cleaning
Filters | Replacement of 0.22 µm filter and cleaning of 0.5 µm filter |  | Check of performance: if necessary replacement of 0.5 µm filter
Compressor | Purge |  | Cleaning and revision
Air conditioner |  |  | Cleaning, filter change and annual control
Electric board and circuit |  |  | Regulatory control
Processes (overflow tanks and regulation of water circulation and distribution) | Verification, cleaning |  | Replacement, if necessary
Sensors (pH, conductivity, O2, temperature) | Cleaning, verification and calibrationif necessary |  | Replacement of consumable items (pH probe, O2 membrane), calibration
Turbidimeter | Cleaning |  | Calibration
Analyzers | Standards and quality check (contamination, signal shift)Supply with chemical reagents Daily check of operation | Change of consumable items (eluents, reagents) Calibration, preventive maintenance | Change of consumable items (columns, tubing) Intervention of manufacturer
Pure or ultra-pure water | Refilling of tanks Checking of water quality |  | Replacement of cartridges, cleaning
Chemical wastes | Collection and removal | Collection and removal
Online notebook | Registration of all operations and interventions |  | Archiving the notebook